## Turbine
TRANSWESTERN PIPELINE COMPANY
RED ROCK EXPANSION PROJECT
KINGMAN COMPRESSOR STATION
Table 1
TURBINE INFORMATION
Manufacturer: | GE LM2500
Fuel Type: | Sweet Natural Gas
HHV: | 1020 | Btu/scf
Site Elevation: | 5063
Inlet Loss: | 4 | in H2O
Exhaust Loss: | 4 | in H2O
Shaft Power: | 40916 | hp @ 12.8oF (Base Load)
| 33526 | hp @ 60oF (Base Load)
Max Heat Rate: | 9429 | Btu/hp-hr @95oF (50% Load)
| 385.797 | MMBtu/hr | (Max Heat Rate x shp@12.8oF)
Avg Heat Rate: | 6298 | Btu/hp-hr @60oF (Base Load)
| 211.1467 | MMBtu/hr | (Avg Heat Rate x shp@60oF)
Speed: | 6100 | rpm
Max Hourly Fuel: | 0.37823 | MMscf/hr | (Max Heat Rate/HHV)
Avg Hourly Fuel: | 0.20701 | MMscf/hr | (Avg Heat Rate/HHV)
Annual Fuel: | 1813.378 | MMscf/yr | (Avg Fuel x 8760)
Potential Emissions
Temp | Turbine | NOx (as NO2) |  | CO |  | THC
(oF) | Load (%) | (lb/hr) | (tpy) | (lb/hr) | (tpy) | (lb/hr) | (tpy)
0 | Base | 24.6 | 107.748 | 15 | 65.7 | 5.1 | 22.338
0 | 64 | 27.8 | 121.764 | 16.9 | 74.022 | 5.9 | 25.842
0 | 50 | 25.2 | 110.376 | 15.3 | 67.014 | 5.4 | 23.652
12.8 | Base | 24.9 | 109.062 | 15.2 | 66.576 | 5.1 | 22.338
12.8 | 50 | 24.7 | 108.186 | 15 | 65.7 | 5.3 | 23.214
40 | Base | 22.8 | 99.864 | 13.8 | 60.444 | 4.7 | 20.586
40 | 50 | 22.5 | 98.55 | 13.7 | 60.006 | 4.8 | 21.024
60 | Base | 21.2 | 92.856 | 12.9 | 56.502 | 4.4 | 19.272
60 | 50 | 14.5 | 63.51 | 8.8 | 38.544 | 3 | 13.14
95 | Base | 18.5 | 81.03 | 11.3 | 49.494 | 3.8 | 16.644
95 | 50 | 13.1 | 57.378 | 8 | 35.04 | 2.7 | 11.826
| Max Hourly | 27.8 | 121.764 | 16.9 | 74.022 | 5.9 | 25.842
| Base Load Max | 24.9 | 109.062 | 15.2 | 66.576 | 5.1 | 22.338
AP-42 Emission Factors (04/00)
PM | 0.0066 | lb/MMBtu
SO2 | 0.0034 | lb/MMBtu
Formaldehyde | 0.00071 | lb/MMBtu
Proposed Turbine Emissions
| Maximum | Annual
Pollutant | (lb/hr) | (tpy)
NOX | 27.8 | 111.6024 | @base load 80% of time, 64% load 20% of time
CO | 16.9 | 68.0652 | @base load 80% of time, 64% load 20% of time
VOC | 0.59 | 2.3039 | @base load 80% of time, 64% load 20% of time; assume 10% NMHC.
PM | 2.5463 | 6.1038 | @max hourly based on max heat rate, annuals based on avg heat rate
SO2 | 1.3117 | 3.1444 | @max hourly based on max heat rate, annuals based on avg heat rate
Formaldehyde | 0.27392 | 0.65662 | @max hourly based on max heat rate, annuals based on avg heat rate
Proposed Turbine Emissions with 15% Safety Factor
| Maximum | Annual
Pollutant | (lb/hr) | (tpy)
NOX | 31.97 | 128.3428
CO | 19.435 | 78.275
VOC | 0.6785 | 2.6495
PM | 2.9282 | 7.0194
SO2 | 1.5085 | 3.6161
Formaldehyde | 0.315 | 0.75512
Note on C52: Suggested Repair:D41 Suggested Value:121.764
Note on C53: Suggested Repair:F41 Suggested Value:74.022
Note on C54: Suggested Repair:H41*0.1 Suggested Value:2.5842

## Netting 2
TRANSWESTERN PIPELINE COMPANY
RED ROCK EXPANSION PROJECT
KINGMAN COMPRESSOR STATION
1999 Emissions Reported to ADEQ (from EI)
Unit | Nox (tpy) | CO (tpy) | VOC (tpy)
101 | 106.98 | 92 | 1.5
102 | 98.83 | 85 | 1.38
103 | 120.08 | 103.27 | 1.68
121 | 0 | 0 | 0
122 | 0 | 0 | 0
Total | 325.89 | 280.27 | 4.56
2000 Emissions Reported to ADEQ (from EI)
Unit | Nox (tpy) | CO (tpy) | VOC (tpy)
101 | 280.87 | 472.77 | 3.76
102 | 236.95 | 398.84 | 3.17
103 | 214.98 | 361.87 | 2.88
121 | 5.26 | 8.85 | 0.07
122 | 0 | 0 | 0
Total | 738.06 | 1242.33 | 9.88
Last 2-Year Emissions Average (from EIs)
Unit | Nox (tpy) | CO (tpy) | VOC (tpy)
101 | 193.925 | 282.385 | 2.63
102 | 167.89 | 241.92 | 2.275
103 | 167.53 | 232.57 | 2.28
121 | 2.63 | 4.425 | 0.035
122 | 0 | 0 | 0
Total | 531.975 | 761.3 | 7.22
Proposed Emission Increases (tpy)
Turbine | 128.34 | 78.27 | 2.65
Gen Engines | 9.23 | 9.65 | 0.12
TOTAL | 137.57 | 87.92 | 2.77
Contemporaneous Emission Decreases (tpy)
| 531.975 | 761.3 | 7.22
Net Change (Increase - Decrease) (tpy)
| -394.405 | -673.38 | -4.45
Notes:
(1) Proposed NOx, CO, and VOC emissions based on 80/20 split. Turbine will operate at 100% load 80% of the time
and 64% load 20% of the time.
(2) Proposed increases are from proposed turbine and generator engines.
Only one generator engine will be run at a time.
(3) Contemporaneous decreases are from permanent shutdown of Units 101, 102, 103, 121, and 122.